## LOLOM Questions
ADDENDUM 6 ATTACHMENT 1
Rahabilitation of Lalomauga Hydro Plant
| Bid No. SAM EPC LALOM/01 - 2018 |  | Bid Questions and Queries
Question No. | Reference: | Date Generated: | Question: | Date of Response: | Employer/EPC Response:
1 | General | 08.03.18 | Can EPC please provide full drawing set of the station - Civil, Mechanical, Electrical, Controls. | 26 Mar. | All drawings is now available by connect to Zoom.
2 | General | 08.03.18 | Due to information transfer and addendums being submitted in the last week of the prescribed tender period, can EPC please confirm if a tender period extension of time shall be granted? | 26 Mar. | Bid closing date is extended from 9th April to Monday 30th April 2018 at 10am local time.
3 | Machine | 08.03.18 | The Lalomauga machines are not impulse turbines. Reference has been made to nozzles and deflectors in the bid document, however these Francis machines do not have these elements. Confirmation thereof. | 26 Mar. | Turbines are both Francis type. It is confirmed that nozzles and deflectors do not apply to Francis turibnes.
4 | Runner | 08.03.18 | What previous repairs to the runner have been undertaken? What condition of the runner is to be expected? | 26 Mar. | There has not been any recent major overhaul of turbine runners. This bid requires contractor to refurbissh turbines and all its associated equipment.
5 | Guide vanes | 08.03.18 | What condition of guide vanes is to be expected? | 26 Mar. | Conditions of guide vanes are not know. Bidders must allow in their bid to fully refurbish them and not replacing them.
6 | Turbine casing | 08.03.18 | What wear is expected on the head cover and bottom cover? | 26 Mar. | Conditions of bottom and top covers are not know. Bidders must allow in their bid to fully refurbish them and not replacing them.
7 | Turbine shaft | 08.03.18 | What condition is each turbine shaft in and are any repairs expected? | 26 Mar. | Turbine shalfts shall be fully refurbished.
8 | Turbine efficiency | 08.03.18 | Modifications to the turbine may increase efficiency and improve return on investment for EPC. Would an efficiency increase be valued by EPC and, if so how would this be valued? | 26 Mar. | Requirement of this bid is to refurbish turbine to its standard efficiency with modifications. As options, bidders can offer alternative modifications to increase efficiency. Bidders much provide alternative price to do this as option.
9 |  | 08.03.18 | Turbine shaft seal, is the existing seal effective and what repairs are invisiged to either the shaft in this region or the seal elements themselves | 26 Mar. | That is the determineation that bidder must state in detail what refubishment they intend to perform to guarantee machine output.
10 | Turbine casing | 08.03.18 | Is any erosion or cavitation erosion expected in the turbine casing or draft tube? | 26 Mar. | We are certain there is erosion or cavitation. Bid requires bidders to allow for refurbishment in order to repair these faults.
11 | PIV installation | 08.03.18 | Works for the PIV installation are Mehcanical, Electrical and Controls. Request to have this brought into the 'Lot 1' package of works. | 26 Mar. | Installation of PIV remains with Lot 2.
12 | MIV | 08.03.18 | The Main Inlet Valve appears to be a ball valve. Can you please confirm this and the anticipated refurbishment requirements? Please provide drawings per item 1.0 above. | 26 Mar. | to be advised
13 | Turbine/Generator system | 08.03.18 | Does the flywheel, rotor and runner need to be dynamically balanced? | 26 Mar. | No, this is not necessary.
14 | Generator | 08.03.18 | Are there any electrical repairs required in the generator? | 26 Mar. | There are no majkor repairs needed done on gnerators except they should be fully cleaned and tested.
15 | General Mechanical | 08.03.18 | What paint system is required for the refurbished mechanical parts - wetted and non-wetted? | 26 Mar. | Dark hydro blue.
16 | General Electrical | 08.03.18 | Can cabling be re-used? Or are new cables required? Please clarify magnitude. | 26 Mar. | Reuse old cables. But contractor must test them. Also contractor shall make sure no cable is damaged during disasssembly of generators. If a cable is damaged, contractor shall replace it at own cost, not EPCs.
17 | Controls | 08.03.18 | Please clarify the function of the over velocity device at the head pond. | 26 Mar. | There is not over velocity device at th4e headpond. PIV will be installed on exit of turnnel.
18 | Unit 2 bearings | 08.03.18 | Unit 2 has experienced on going failures of the thrust bearings. Some attempts of correction were mentioned at the bid meeting. Please further elaborate on the issue and clarify if some sort of design issue is anticipated here. | 26 Mar. | There is no redesign issue involved. Thrust collars will be replace in March. EPC requires new collar to be reused.
19 | HPU & Governer | 08.03.18 | If new HPU and governers do not require concrete pedestals, are the concrete pedestals required for old equipment required to be removed? | 26 Mar. | That is responsibility of contractor to remove concrete pedestals. Bidders must allow for this in their bid.
20 | Generator | 08.03.18 | Is the heat loading in the power house satisfactory or does EPC wish to duct the generator exhausts to the outside of the building? | 26 Mar. | Heat loading for the powerhouse is acceptable. There is no need to duct generator exhaust outside.
21 | Isolation of plant | 08.03.18 | Please explain the method of isolation of the penstock from the headpond during the works. Also pleased confirm blanking plates available for the powerhouse after removal of the MIVs | 26 Mar. | Headpond will be emptied when this work is carried out. Water at the intakes will be shutoff. Contractor will provide blanking plates to install during construction.
22 | Pricing schedule | 08.03.18 | Pricing schedule for Lot 2 is incorrectly labelled as Lot 1. Lot 1 pricing schedule is not included in the documents. Please provide this. | 26 Mar. | See Bid Forms attached
23 | Over Velocity device and Valve | 08.03.18 | What is the expected condition of the valve and actuation elements that is to used for this service, are repairs required before re-use | 26 Mar. | Bidders to access from information provide and allow for in bid repairs to be carried out. Bidders must provide in detail repairs to be done.
24 | Over Velocity device and Valve | 08.03.18 | Please clarify the method required for over velocity sensing | 26 Mar. | Bidders must offer method of sensing over velocity.
25 | Average annual Turnover | 08.03.18 | Please specify turn-over figure (BDS does not mention this). | 26 Mar. | Average Annual Turnover shall be: US$2.0 million for LOT 1 and US$1M for LOT 2. Minimum Cash Flow is 60% of contract price. Bidders must provide evidence they have financial resources to perform this contract.
|  |  | Audited Annual Financial Statements | 26th Mar. | Bidders must provide annual financial statements for 3 recent years. Financial Statements to be audited or certified by a registered CPA acceptable to EPC.
26 | Delayed payment rate | 08.03.18 | Please specify interest rate (11.9 Delayed Payment) | 26 Mar. | In the event that the Employer fails to make any payment on its respective due date, the Employer shall pay to the Contractor interest on the amount of such delayed payment at the rate of 0.5 percent (0.5 %) per month for period of delay until payment has been made in full.
27 | Pricing Schedules | 08.03.18 | Please amend Pricing Schedules to include both Lot 1 and Lot 2 preferred line pricing items. Also payment terms refer to Sch. 1-4, but no Pricing Schedules for these. | 26 Mar. | See Bid Forms attached
28 | Bidding Form | 08.03.18 | Please send new Bidding Form as aluded to last week. | 26 Mar. | See Bid Forms attached
29 | Financial Forms | 08.03.18 | Please send new Financial Forms with qualification requirements. | 26 Mar. | Refer to attached Bid Form to be filled in and signed by authorized person of company.
30 | Transformer cable | 08.03.18 | Tidy up of cable at transformer yard' is currently in Lot 2 however is an electrical task. Request that this is transferred to Lot 1 therefore. | 26 Mar. | Refer to attachment of this Addendum 6, which list scope of work for LOT 1 Part 1 and Part 2, and LOT 2 Part 3