Pre-bid Questionnaire 1

Sub: Clarifications on Tender #02/2025

As per the discussions during the Pre-bid meeting at the PPA office regarding the Tender # 02/2025, thank you for attendance in number. Attached is a list of questions during the Prebid meeting #1, however, to document we have listed below questions and subsequent answers for potential bidders’ information ...

- Geotechnical Report Could you please confirm whether a geotechnical investigation report is required prior to project commencement? This will help us assess soil conditions and foundation design requirements. Geotech report will be made available through the tender link portal.

- Site Marking for Installation Will the exact installation locations be pre-marked or staked out on site to guide our civil and electrical works? Site marking will be provided but, bidders are welcomed to provide alternative proposals in their design

- Drawings and Documentation Will your team be providing typical layout drawings or GA (General Arrangement) drawings to support installation planning and coordination? Bidders are encouraged to provide these requirements in their proposal

- SCADA System Reference Kindly advise if the current SCADA system’s data sheet will be shared for integration reference and compatibility checks. Yes, this will be shared

- Cable Routing Will the cable routes be marked or provided in drawing format to facilitate accurate electrical cabling and trenching? This can be provide but it is preferred that bidder provides his proposal.

- Generator Type Preference Please confirm whether you require silent-type containerized generators or open-type units, considering site noise restrictions and environmental factors.  As stated during the meeting, we would prefer open type units in a closed shed.

- How many hrs of usage will be required by each of the two generators? As stated below, this will depend on the Solar Irradiance. Estimate of around 120 hours per week.

- Operational Hours Could you specify the expected daily or weekly operating hours for each of the two generators? This will guide sizing, fuel planning, and maintenance scheduling. Operational hours will vary, depending on situation’s that may arise. But both Gen Sets will be on fulltime standby See above.

- Load Distribution What percentage of load is expected to be handled by each generator individually and when operating in parallel? This will help us configure the synchronization and load-sharing parameters. These generators will be expected to be loaded up to 100% of its rated capacity. Generators are to be loaded equally when operating in parallel.

- Installation Layout Details Will NUC be providing details regarding generator orientation, spacing between units, day tank capacities, and installation locations? This should be part of the bidders’ proposals.

- Site Utilities Will water and electricity be made available on site to support construction and commissioning activities? Water & Electricity will be provided. However, drinking water will not be available

- Contractor Facilities Is there a toilet facility available on site for contractor use during the project period? Toilet facilities is available at the site

- Pre-Bid Site Visit Support If a pre-bid site visit is required, could you kindly assist with site access, invitation letters, and visa facilitation where applicable? Attached is the Nauru business visa which can be filled and submitted to apenisa.manuduitagi@nuc.com.nr

- Working Hours and Restrictions Are there any specific site timing restrictions or working hour limitations we should be aware of during the execution phase? No working hour restriction in place. Successful bidder will decide hours of work