## SEL351S
MR93/2026
Chasis And Mounting
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | Horizontal | Vertical | Chasis | User Interface | User Interface Trip and Close Pushbuttons | User Interface Configurable Labels | Power Supply | Communication Interface | Communication Protocol | Secondary Input Current | Control Input Voltage | I/O Board
1 | 11kV Feeder Protection & 33kV Sub-transmission Network, Backup Protection Relay | SEL-351S-7 | 0351S7XCD3F1322 | 0351S7XHE3J1362 | 351S#3PQE | Standard plus Power Elements, Voltage Sag/Swell/Interruption | Horizontal Rack Mount | N/A | 3U | Standard with USB | Outdoor Pushbuttons The breaker position indicating LEDs of the Indoor SafeLock Trip/Close Pushbutton option have a white diffusing material over the LED which creates a wide viewing angle. The breaker position indicating LEDs of the Outdoor SafeLock Trip/Close Pushbutton option have a high-intensity LED and translucent diffusing material for improved visibility in direct sun light. | Yes | 48/125 Vdc or 120 Vac | Two 10/100 Base-T and One Fiber-Optic MM ST Serial Port | Standard Plus IEC 61850 | 1 Amp Phase, 1 Amp Neutral | 110 Vdc | Additional 12 High I/C Outputs, 8 Inputs
2 |  |  |  | 0351S7X3E3J1362 | 351S#JFQH | Standard plus Power Elements, Voltage Sag/Swell/Interruption | Horizontal Panel Mount | N/A | 3U | Standard with USB | Outdoor Pushbuttons The breaker position indicating LEDs of the Indoor SafeLock Trip/Close Pushbutton option have a white diffusing material over the LED which creates a wide viewing angle. The breaker position indicating LEDs of the Outdoor SafeLock Trip/Close Pushbutton option have a high-intensity LED and translucent diffusing material for improved visibility in direct sun light. | Yes | 48/125 Vdc or 120 Vac | Two 10/100 Base-T and One Fiber-Optic MM ST Serial Port | Standard Plus IEC 61850 | 1 Amp Phase, 1 Amp Neutral | 110 Vdc | Additional 12 High I/C Outputs, 8 Inputs
3 |  |  |  | 0351S7X4E3J1362 | 351S#3HJQ | Standard plus Power Elements, Voltage Sag/Swell/Interruption | N/A | Vertical Panel Mount | 3U | Standard with USB | Outdoor Pushbuttons The breaker position indicating LEDs of the Indoor SafeLock Trip/Close Pushbutton option have a white diffusing material over the LED which creates a wide viewing angle. The breaker position indicating LEDs of the Outdoor SafeLock Trip/Close Pushbutton option have a high-intensity LED and translucent diffusing material for improved visibility in direct sun light. | Yes | 48/125 Vdc or 120 Vac | Two 10/100 Base-T and One Fiber-Optic MM ST Serial Port | Standard Plus IEC 61850 | 1 Amp Phase, 1 Amp Neutral | 110 Vdc | Additional 12 High I/C Outputs, 8 Inputs
4 |  |  |  | 0351S7X5E3J1362 | 351S#YGNY | Standard plus Power Elements, Voltage Sag/Swell/Interruption | Horizontal Projection Panel Mount | N/A | 3U | Standard with USB | Outdoor Pushbuttons The breaker position indicating LEDs of the Indoor SafeLock Trip/Close Pushbutton option have a white diffusing material over the LED which creates a wide viewing angle. The breaker position indicating LEDs of the Outdoor SafeLock Trip/Close Pushbutton option have a high-intensity LED and translucent diffusing material for improved visibility in direct sun light. | Yes | 48/125 Vdc or 120 Vac | Two 10/100 Base-T and One Fiber-Optic MM ST Serial Port | Standard Plus IEC 61850 | 1 Amp Phase, 1 Amp Neutral | 110 Vdc | Additional 12 High I/C Outputs, 8 Inputs
5 |  |  |  | 0351A0H6X3J13X2 | 351A#7LBM | Standard | Horizontal Rack Mount | N/A | 2U | Standard Interface including USB plus Indoor SafeLock Trip/Close Pushbuttons | N/A | N/A | 48/125 Vdc or 120 Vac | Two 10/100 Base-T and One Fiber-Optic MM ST Serial Port | Standard Plus IEC 61850 | 1 Amp Phase, 1 Amp Neutral | 110 Vdc | N/A
6 |  |  |  | 0351A036X3J13X2 | 351A#VB3Y | Standard | Horizontal Panel Mount | N/A | 2U | Standard Interface including USB plus Indoor SafeLock Trip/Close Pushbuttons | N/A | N/A | 48/125 Vdc or 120 Vac | Two 10/100 Base-T and One Fiber-Optic MM ST Serial Port | Standard Plus IEC 61850 | 1 Amp Phase, 1 Amp Neutral | 110 Vdc | N/A
7 |  |  |  | 0351A046X3J13X2 | 351A#FFRR | Standard | N/A | Vertical Panel Mount Vertical panel mount has no LCD | 2U | Standard Interface including USB plus Indoor SafeLock Trip/Close Pushbuttons | N/A | N/A | 48/125 Vdc or 120 Vac | Two 10/100 Base-T and One Fiber-Optic MM ST Serial Port | Standard Plus IEC 61850 | 1 Amp Phase, 1 Amp Neutral | 110 Vdc | N/A
8 |  |  |  | 0351A056X3J13X2 | 351A#T98X | Standard | Horizontal Projection Panel Mount | N/A | 2U | Standard Interface including USB plus Indoor SafeLock Trip/Close Pushbuttons | N/A | N/A | 48/125 Vdc or 120 Vac | Two 10/100 Base-T and One Fiber-Optic MM ST Serial Port | Standard Plus IEC 61850 | 1 Amp Phase, 1 Amp Neutral | 110 Vdc | N/A

## SEL 387E
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | I/O Board, Chasis | Power Supply | Seconday Input Voltage | Secondary Input Current | Mounting | Conformal Coat | Control Input Voltage | Communication Protocol | Accessories
1 | Two Winding or Three Winding Transformer Protection (33kV/11kV or 33kV/6.6kV) | SEL-387E | 0387E014X1H2235 | 0387E013X1H2235 | 387E#RPLW | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Horizontal Rack Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 100BASE-FX Ethernet Ports and IEC 61850
2 |  |  |  | 0387E013X1H2234 | 387E#BHH2 | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Horizontal Rack Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 10/100BASE-T Ethernet Ports, and IEC 61850
3 |  |  |  | 0387E013X132235 | 387E#V0JT | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Horizontal Panel Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 100BASE-FX Ethernet Ports and IEC 61850
4 |  |  |  | 0387E013X132234 | 387E#3ML6 | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Horizontal Panel Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 10/100BASE-T Ethernet Ports, and IEC 61850
5 |  |  |  | 0387E013X152235 | 387E#C365 | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Horizontal Projection Panel Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 100BASE-FX Ethernet Ports and IEC 61850
6 |  |  |  | 0387E013X152234 | 387E#D3V0 | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Horizontal Projection Panel Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 10/100BASE-T Ethernet Ports, and IEC 61850
7 |  |  |  | 0387E013X1V2235 | 387E#QX9N | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Vertical Rack Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 100BASE-FX Ethernet Ports and IEC 61850
8 |  |  |  | 0387E013X1V2234 | 387E#24YR | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Vertical Rack Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 10/100BASE-T Ethernet Ports, and IEC 61850
9 |  |  |  | 0387E013X142235 | 387E#3CKC | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Vertical Panel Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 100BASE-FX Ethernet Ports and IEC 61850
10 |  |  |  | 0387E013X142234 | 387E#F8EY | Standard | 3U, Additional 12 Std Outputs, 8 Inputs | 48/125 Vdc or 125 Vac | 300 Vac Maximum (Wye or Delta) | 1 A Phase | Vertical Panel Mount | Conformally Coated Circuit Boards | 110 Vdc | Serial SEL ASCII, SEL Fast Message, and DNP3 Level 2 Slave with Two 10/100BASE-T Ethernet Ports, and IEC 61850

## SEL 487E
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | Connector Type | Secondary Inputs | Conformal Coat | Power Supply | AC Input Card 1 Configuration (Current Channels S, T, U) | AC Input Card 2 Configuration (Current Channels W, X,Y) | Ethernet Communications Protocols | Ethernet Connection Options | Mainboard Input Voltage | Mounting | Chasis | I/O Board Position B | I/0 Board Position B Input Voltage | I/O Board Position C | I/0 Board Position C Input Voltage | I/O Board Position D and E (Same IO Type, Utilizing the Selected IO Board C Input Voltage)
1 | 132/33kV Transformer Main Protection (3 Winding) | SEL 487E | 0487E32648XXC3X3H673XXX | 0487E32648XXC1X3H673XXX | 487E#YKQK | Standard | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye) | Conformally Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | S=1A, T=1A, U=1A | W=1A, X=1A, Y=1A,1A,1A (4) Current Channel Y is comprised of three single-phase neutral current inputs. (5) When using the Y current channels for synchrophasor data, all Y channel currents must have the same nominal current rating (1 A, 1 A, 1 A or 5 A, 5 A, 5 A) to provide proper synchrophasor scaling. AC Input Card 2 Configuration options 1, 4, 5, or 8 meet this criteria. | FTP, Telnet, DNP3 LAN/WAN, PRP and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 10/100BASE-T Connectors (6) Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Rack Mount | 6U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs,13 High-Current Interrupting Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | NA
2 |  |  |  | 0487E32648XXC3X3H673XXX | 487E#FB0L | Standard | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye) | Conformally Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | S=1A, T=1A, U=1A | W=1A, X=1A, Y=1A,1A,1A (4) Current Channel Y is comprised of three single-phase neutral current inputs. (5) When using the Y current channels for synchrophasor data, all Y channel currents must have the same nominal current rating (1 A, 1 A, 1 A or 5 A, 5 A, 5 A) to provide proper synchrophasor scaling. AC Input Card 2 Configuration options 1, 4, 5, or 8 meet this criteria. | FTP, Telnet, DNP3 LAN/WAN, PRP and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 100BASE-FX Connectors (6) Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Rack Mount | 6U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs,13 High-Current Interrupting Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | NA
3 |  |  |  | 0487E32648XXC1X3H77323X | 487E#9BTA | Standard | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye) | Conformally Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | S=1A, T=1A, U=1A | W=1A, X=1A, Y=1A,1A,1A (4) Current Channel Y is comprised of three single-phase neutral current inputs. (5) When using the Y current channels for synchrophasor data, all Y channel currents must have the same nominal current rating (1 A, 1 A, 1 A or 5 A, 5 A, 5 A) to provide proper synchrophasor scaling. AC Input Card 2 Configuration options 1, 4, 5, or 8 meet this criteria. | FTP, Telnet, DNP3 LAN/WAN, PRP and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 10/100BASE-T Connectors (6) Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Rack Mount | 7U, Up to Two Additional I/O Boards | 8 Optoisolated Independent Level-Sensitive Inputs,13 High-Current Interrupting Form A, 2 Standard Form C Outputs | 110 Vdc | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA
4 |  |  |  | 0487E32648XXC3X3H77323X | 487E#6CWG | Standard | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye) | Conformally Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | S=1A, T=1A, U=1A | W=1A, X=1A, Y=1A,1A,1A (4) Current Channel Y is comprised of three single-phase neutral current inputs. (5) When using the Y current channels for synchrophasor data, all Y channel currents must have the same nominal current rating (1 A, 1 A, 1 A or 5 A, 5 A, 5 A) to provide proper synchrophasor scaling. AC Input Card 2 Configuration options 1, 4, 5, or 8 meet this criteria. | FTP, Telnet, DNP3 LAN/WAN, PRP and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 100BASE-FX Connectors (6) Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Rack Mount | 7U, Up to Two Additional I/O Boards | 8 Optoisolated Independent Level-Sensitive Inputs,13 High-Current Interrupting Form A, 2 Standard Form C Outputs | 110 Vdc | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA

## SEL311L
MR93/2026
Mounting
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | Chasis | Horizontal | Vertical | Line Current Differential Communications Channel X | Line Current Differential Communications Channel Y | Power Supply | Secondary Input Voltage | Secondary Input Current | Control Input Voltage | I/O Board | Communications Protocol | Conformal Coat
1 | 33kV Sub-transmission Line Main Protection | SEL-311L | 0311L7JEE3213252X | 0311L7JEE3213242X | 311L#LWY9 | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 4U | Horizontal Rack Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | 8 Inputs, 12 Standard Outputs | Standard plus Serial DNP3, Two 10/100BASE-T Ethernet Ports and IEC 61850 | Yes
2 |  |  |  | 0311L7JEE3213252X | 311L#KB2A | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 4U | Horizontal Rack Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | 8 Inputs, 12 Standard Outputs | Standard plus Serial DNP3, Two 100BASE-FX Ethernet Ports and IEC 61850 | Yes
3 |  |  |  | 0311L7KEE3213242X | 311L#R6CR | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 4U | Horizontal Panel Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | 8 Inputs, 12 Standard Outputs | Standard plus Serial DNP3, Two 10/100BASE-T Ethernet Ports and IEC 61850 | Yes
4 |  |  |  | 0311L7KEE3213252X | 311L#22Q5 | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 4U | Horizontal Panel Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | 8 Inputs, 12 Standard Outputs | Standard plus Serial DNP3, Two 100BASE-FX Ethernet Ports and IEC 61850 | Yes
5 |  |  |  | 0311L7LEE3213242X | 311L#0MVV | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 4U | NA | Vertical Panel Mount | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | 8 Inputs, 12 Standard Outputs | Standard plus Serial DNP3, Two 10/100BASE-T Ethernet Ports and IEC 61850 | Yes
6 |  |  |  | 0311L7LEE3213252X | 311L#EAJ0 | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 4U | NA | Vertical Panel Mount | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | 8 Inputs, 12 Standard Outputs | Standard plus Serial DNP3, Two 100BASE-FX Ethernet Ports and IEC 61850 | Yes
7 |  |  |  | 0311L7NEE3213242X | 311L#H9AC | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 4U | Horizontal Projection Panel Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | 8 Inputs, 12 Standard Outputs | Standard plus Serial DNP3, Two 10/100BASE-T Ethernet Ports and IEC 61850 | Yes
8 |  |  |  | 0311L7NEE3213252X | 311L#NTM7 | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 4U | Horizontal Projection Panel Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | 8 Inputs, 12 Standard Outputs |  | Yes
9 |  |  |  | 0311L7HEE3213X42X | 311L#0VKE | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 3U | Horizontal Rack Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | No Additional I/O | Standard plus Serial DNP3, Two 10/100BASE-T Ethernet Ports and IEC 61850 | Yes
10 |  |  |  | 0311L7HEE3213X52X | 311L#7FCN | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 3U | Horizontal Rack Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | No Additional I/O | Standard plus Serial DNP3, Two 100BASE-FX Ethernet Ports and IEC 61850 | Yes
11 |  |  |  | 0311L73EE3213X42X | 311L#3L0H | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 3U | Horizontal Panel Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | No Additional I/O | Standard plus Serial DNP3, Two 10/100BASE-T Ethernet Ports and IEC 61850 | Yes
12 |  |  |  | 0311L73EE3213X52X | 311L#MNEX | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 3U | Horizontal Panel Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | No Additional I/O | Standard plus Serial DNP3, Two 100BASE-FX Ethernet Ports and IEC 61850 | Yes
13 |  |  |  | 0311L74EE3213X42X | 311L#81N8 | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 3U | NA | Vertical Panel Mount | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | No Additional I/O | Standard plus Serial DNP3, Two 10/100BASE-T Ethernet Ports and IEC 61850 | Yes
14 |  |  |  | 0311L74EE3213X52X | 311L#FH57 | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 3U | NA | Vertical Panel Mount | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | No Additional I/O | Standard plus Serial DNP3, Two 100BASE-FX Ethernet Ports and IEC 61850 | Yes
15 |  |  |  | 0311L75EE3213X42X | 311L#T12M | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 3U | Horizontal Projection Panel Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | No Additional I/O | Standard plus Serial DNP3, Two 10/100BASE-T Ethernet Ports and IEC 61850 | Yes
16 |  |  |  | 0311L75EE3213X52X | 311L#PXA2 | Standard with Improved Functions, Single-Pole Differential, and Single-Pole Zone 1 Distance Backup Protection | 3U | Horizontal Projection Panel Mount | NA | 1550nm Fiber | 1550nm Fiber | 48/125 Vdc or 125 Vac | Wye-Connected Va, Vb, and Vc | 1 Amp Phase and 1 Amp Polarizing Current Input | 110 Vdc | No Additional I/O | Standard plus Serial DNP3, Two 100BASE-FX Ethernet Ports and IEC 61850 | Yes

## SEL411L
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | Power Supply | Connector Type | Secondary Inputs | Ethernet Communications Protocols and 87L Line Current Differential | Ethernet Connection Options | Serial Line Current Differential Communications Channel 1 | Serial Line Current Differential Communications Channel 2 | Mounting | Chasis | I/O Board Position B for 4U, 5U, 6U or 7U Chasis | I/O Board Position B Input Voltage | I/O Board Position C for 4U, 5U, 6U or 7U Chasis | I/O Board Position C Input Voltage | I/O Board Position D and E for 6U or 7U Chasis | I/O Board Position D and E Input Voltage | Conformal Coat
1 | 33kV Sub-transmission Line Main Protection | SEL-411L | 0411L126X1C8EEXH52323XX | 0411L126X1C8EEXH52323XX | 411L#YWWN | Standard Current Differential and Distance Elements, Plus Sub-cycle Distance Elements, Series Compensation Logic, TW Fault Locating for Single/Dual Breaker, Single/Three Pole Tripping Applications | 125-250 Vdc or 110-240 Vac | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye), 1 A Phase | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN and IEC 61850 | Two 10/100BASE-T and Two 100BASE-FX Connectors Ports 5A and 5B can be configured for line current differential communication or for IEEE Precision Time Protocol (PTP). If PTP is enabled, 87L over Ethernet will be performed on Ports C, D instead of A, B. PTP is only available on Ports A, B. Ports 5A and 5C are dedicated as 100BASE-FX and Ports 5B and 5D are dedicated as 10/100BASE-T. | 1550 nm Fiber | 1550 nm Fiber | Horizontal Rack Mount | 5U, Up to Two I/O Boards | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | YES
2 |  |  |  | 0411L126X1C9EEXH52323XX | 411L#WLWT | Standard Current Differential and Distance Elements, Plus Sub-cycle Distance Elements, Series Compensation Logic, TW Fault Locating for Single/Dual Breaker, Single/Three Pole Tripping Applications | 125-250 Vdc or 110-240 Vac | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye), 1 A Phase | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN and IEC 61850 | Two 100/1000BASE and Three 100BASE SFP Ports (Order SFP Transceivers Separately) | 1550 nm Fiber | 1550 nm Fiber | Horizontal Rack Mount | 5U, Up to Two I/O Boards | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | YES

## SEL-421
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | Power Supply | Connector Type | Secondary Inputs | Ethernet Communications Protocols | Ethernet Connection Options | Mainboard Input Voltage | Mounting | Chasis | I/O Board Position B for 4U or 5U | I/O Board Position B Input Voltage | I/O Board Position C for 5U Chasis Only | I/O Board Position C Input Voltage | Conformal Coat
1 | 132kV Transmission Line Second Main Protection | SEL-421 | 04215611XC3X3H26XXX2X | 04215611XC3X3H26XXX2X | 421#94HN | Plus Sub-Cycle Elements, Series Compensation Logic, and Full Automation Replaces SEL-421-0, -3 | 125-250 Vdc or 110-240 Vac | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye), 1 A Phase | FTP, Telnet, Synchrophasors, DNP3, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 100BASE-FX Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc Mainboard Configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs and 7 Optoisolated Level-Sensitive Inputs. | Horizontal Rack Mount | 4U, Up to One Additional I/O Board | 8 Independent Inputs, 13 High-Current Interrupting Form A, 2 Standard Form C Outputs | User-Settable Pickup Voltage Level | NA | NA | Conformal Coated Circuit Boards
2 |  |  |  | 04215611XC1X3H26XXX2X | 421#7VY6 | Plus Sub-Cycle Elements, Series Compensation Logic, and Full Automation Replaces SEL-421-0, -3 | 125-250 Vdc or 110-240 Vac | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye), 1 A Phase | FTP, Telnet, Synchrophasors, DNP3, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 10/100BASE-T Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc Mainboard Configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs and 7 Optoisolated Level-Sensitive Inputs. | Horizontal Rack Mount | 4U, Up to One Additional I/O Board | 8 Independent Inputs, 13 High-Current Interrupting Form A, 2 Standard Form C Outputs | User-Settable Pickup Voltage Level | NA | NA | Conformal Coated Circuit Boards
3 |  |  |  | 04215611XC3X3H1XXXX2X | 421#5YRD | Plus Sub-Cycle Elements, Series Compensation Logic, and Full Automation Replaces SEL-421-0, -3 | 125-250 Vdc or 110-240 Vac | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye), 1 A Phase | FTP, Telnet, Synchrophasors, DNP3, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 100BASE-FX Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc Mainboard Configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs and 7 Optoisolated Level-Sensitive Inputs. | Horizontal Rack Mount | 3U, Standard I/O | NA | NA | NA | NA | Conformal Coated Circuit Boards
4 |  |  |  | 04215611XC1X3H1XXXX2X | 421#ELMY | Plus Sub-Cycle Elements, Series Compensation Logic, and Full Automation Replaces SEL-421-0, -3 | 125-250 Vdc or 110-240 Vac | Screw Terminal Block | 300 V Phase - Neutral Maximum (Wye), 1 A Phase | FTP, Telnet, Synchrophasors, DNP3, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 10/100BASE-T Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc Mainboard Configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs and 7 Optoisolated Level-Sensitive Inputs. | Horizontal Rack Mount | 3U, Standard I/O | NA | NA | NA | NA | Conformal Coated Circuit Boards

## SEL-700G
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Model Options | User Interface | Front Panel | Slot A Power Supply Voltage | Slot A Digital Input Voltage | Slot B Ethernet (Port 1) | Slot B Rear Serial Port (Port 3) | IEC 61850 Protocol | DNP3 Protocol | IEC 60870-5-103 Protocol | EtherNet/IP Protocol | Slot C | Slot C Digital Input Voltage | Slot D | Slot D Input Voltage | Slot E | Slot E Digital Input Voltage | Slot Z Current and/or Voltage Inputs | Conformal Coat
1 | Generator Protection Relay | SEL-700G | 0700G11D1D9X72810431 | 0700G11D1D9X72810431 | 700G#GK8F | 700G1+, Basic Generator Protection plus 87, Gen 25, 64G, 21, 78, 78VS, Auto Synchronizer | English | 2x16 LCD With 8 Pushbuttons | 110-250 Vdc (110-240 Vac); 50/60 Hz | 110 Vdc/Vac | Single 100BASE-FX MM LC Ethernet The protocols SNTP, IEEE 1588-2008 firmware-based PTP and Modbus TCP are included. | EIA-232 | Yes | Yes | No | No | 4 DI / 4 DO Electromechanical (Form A) | 110 Vdc/Vac | 10 RTD Inputs | NA | 3-Phase 1 Amp AC Current Input / Vsync Input and Vn (300 Vac) Input (SELECT 3 ACI / 2 AVI) | NA | 3-Phase 1 Amp AC Current Input / 1 Amp Neutral AC Current Input / 3-Phase AC Voltage (300 Vac) (SELECT 4 ACI / 3 AVI) | Yes
2 |  |  |  | 0700G11D1D9X72810631 | 700G#5FG4 | 700G1+, Basic Generator Protection plus 87, Gen 25, 64G, 21, 78, 78VS, Auto Synchronizer | English | 2x16 LCD With 8 Pushbuttons | 110-250 Vdc (110-240 Vac); 50/60 Hz | 110 Vdc/Vac | Dual 10/100BASE-T Ethernet The protocols SNTP, IEEE 1588-2008 firmware-based PTP, PRP, and Modbus TCP are included. | EIA-232 | Yes | Yes | No | No | 4 DI / 4 DO Electromechanical (Form A) | 110 Vdc/Vac | 10 RTD Inputs | NA | 3-Phase 1 Amp AC Current Input / Vsync Input and Vn (300 Vac) Input (SELECT 3 ACI / 2 AVI) | NA | 3-Phase 1 Amp AC Current Input / 1 Amp Neutral AC Current Input / 3-Phase AC Voltage (300 Vac) (SELECT 4 ACI / 3 AVI) | Yes
3 |  |  |  | 0700G11D1D9X72810831 | 700G#2JH2 | 700G1+, Basic Generator Protection plus 87, Gen 25, 64G, 21, 78, 78VS, Auto Synchronizer | English | 2x16 LCD With 8 Pushbuttons | 110-250 Vdc (110-240 Vac); 50/60 Hz | 110 Vdc/Vac | Dual 100BASE-FX MM LC Ethernet The protocols SNTP, IEEE 1588-2008 firmware-based PTP, PRP, and Modbus TCP are included. | EIA-232 | Yes | Yes | No | No | 4 DI / 4 DO Electromechanical (Form A) | 110 Vdc/Vac | 10 RTD Inputs | NA | 3-Phase 1 Amp AC Current Input / Vsync Input and Vn (300 Vac) Input (SELECT 3 ACI / 2 AVI) | NA | 3-Phase 1 Amp AC Current Input / 1 Amp Neutral AC Current Input / 3-Phase AC Voltage (300 Vac) (SELECT 4 ACI / 3 AVI) | Yes

## SEL-587Z
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | Conformal Coat | Power Supply; Control Input Voltage | Energy - Clamping MOVs | Secondary Input Current | Mounting | Communications Port | Communications Protocol
1 | High Impedance Busbar Protection Relay (11kV or 33kV) | SEL-587Z | 0587Z02321H2XX | 0587Z0X111H12XX | 587Z#NK9H | Standard | No | 24 Vdc; 24 Vdc | 1 MOV - 2500 J, 2000 V | 1 A Phase | Horizontal Rack Mount | EIA-232 Front and Rear Port | Standard Plus Modbus RTU
2 |  |  |  | 0587Z0X111312XX | 587Z#D9PA | Standard | No | 24 Vdc; 24 Vdc | 1 MOV - 2500 J, 2000 V | 1 A Phase | Horizontal Panel Mount | EIA-232 Front and Rear Port | Standard Plus Modbus RTU
3 |  |  |  | 0587Z0X111512XX | 587Z#HGLL | Standard | No | 24 Vdc; 24 Vdc | 1 MOV - 2500 J, 2000 V | 1 A Phase | Horizontal Projection Panel Mount | EIA-232 Front and Rear Port | Standard Plus Modbus RTU

## SEL487B
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | Conformal Coat | Power Supply | Connector Type | Secondary Input Current | AC Input Channels | Ethernet Communications Protocols | Ethernet Communications Protocols | Mainboard Input Voltage | Mounting | Chassis | I/O Board Slot B Control Input Voltage | I/O Board Slot B Contact Outputs | I/O Board Slot C Control Input Voltage | I/O Board Slot C Contact Outputs | I/O Board Slot D Control Input Voltage | I/O Board Slot D Contact Outputs | I/O Board Slot E Control Input Voltage | I/O Board Slot E Contact Outputs | DMA Bundle
1 | Low Impedance Busbar Protection Relay (132kV) | SEL-487B | 0487B124X12XC1XD37NNXXX | 0487B124X12XC1XD37NNXXX | 487B#E6GH | Standard | Conformally Coated Circuit Boards | 48-125 Vdc or 110-120 Vac | Screw Terminal Block | 1 A Phase | 3 AC Voltage, 21 AC Current | FTP, Telnet, DNP3 LAN/WAN, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 10/100BASE-T Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Panel Mount | 7U,Front Panel with 16 Target LEDs, 8 Operator Control Pushbuttons. 7U mounting option supports up to two I/O boards. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | None | NA | None | NA | No
2 |  |  |  | 0487B124X12XC3XD37NNXXX | 487B#ML85 | Standard | Conformally Coated Circuit Boards | 48-125 Vdc or 110-120 Vac | Screw Terminal Block | 1 A Phase | 3 AC Voltage, 21 AC Current | FTP, Telnet, DNP3 LAN/WAN, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 100BASE-FX Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Panel Mount | 7U,Front Panel with 16 Target LEDs, 8 Operator Control Pushbuttons. 7U mounting option supports up to two I/O boards. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | None | NA | None | NA | No
3 |  |  |  | 0487B124X12XC1XDH7NNXXX | 487B#F8R1 | Standard | Conformally Coated Circuit Boards | 48-125 Vdc or 110-120 Vac | Screw Terminal Block | 1 A Phase | 3 AC Voltage, 21 AC Current | FTP, Telnet, DNP3 LAN/WAN, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 10/100BASE-T Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Rack Mount | 7U,Front Panel with 16 Target LEDs, 8 Operator Control Pushbuttons. 7U mounting option supports up to two I/O boards. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | None | NA | None | NA | No
|  |  |  | 0487B124X12XC1XDHANNXXX | 487B#1CPB | Standard | Conformally Coated Circuit Boards | 48-125 Vdc or 110-120 Vac | Screw Terminal Block | 1 A Phase | 3 AC Voltage, 21 AC Current | FTP, Telnet, DNP3 LAN/WAN, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 10/100BASE-T Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Rack Mount | 9U,Front Panel with 24 Target LEDs, 12 Operator Control Pushbuttons and Tri-Color LEDS. 9U mounting option supports up to four I/O boards. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | None | NA | None | NA | No
|  |  |  | 0487B124X12XC1XD3ANNXXX | 487B#M64A | Standard | Conformally Coated Circuit Boards | 48-125 Vdc or 110-120 Vac | Screw Terminal Block | 1 A Phase | 3 AC Voltage, 21 AC Current | FTP, Telnet, DNP3 LAN/WAN, and IEC 61850 | Ports 5A, 5B With PTP: Ethernet Card With Two 10/100BASE-T Connectors Only two Ethernet ports will be populated based on the Ethernet Connection Options Selection. IEEE Precision Time Protocol (PTP) is only available on Port 5A and 5B. | 110 Vdc | Horizontal Panel Mount | 9U,Front Panel with 24 Target LEDs, 12 Operator Control Pushbuttons and Tri-Color LEDS. 9U mounting option supports up to four I/O boards. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | 110 Vdc or Vac | 8 Standard Output Contacts 18 Common Inputs, 6 Independent Inputs, 8 Standard Form A Outputs. | None | NA | None | NA | No

## SEL487V
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Firmware | Conformal Coat | Power Supply | Connector Type | Secondary Input Current | AC Input Channels | Ethernet Communications Protocols | Ethernet Communications Protocols | Mainboard Input Voltage | Mounting | Chassis | I/O Board Position B For 4U or 5U Chasis | I/O Board Position B Input Voltage | I/O Board Position C For 5U Chasis Only | I/O Board Position C Input Voltage | DMA Bundle
1 | Capacitor Bank Protection Relay | SEL-487V | 0487V126111XC4X3H423XXX | 0487V126111XC4X3H423XXX | 487V#H8JK | Standard Plus Automatic Voltage Control and VSSI Reporting | Conformal Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | Screw-Terminal Block | 300 V Phase-Neutral Maximum (Wye), 1 A W , 1 A X Current Terminals | 6 AC Voltage, 6 AC Current | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN, and IEC 61850 | Ethernet Card With One 100BASE-FX, One 10/100BASE-T Connector | 110 Vdc Mainboard configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs, and 7 Optoisolated Level-Sensitive Inputs. | Horizontal Rack Mount | 4U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | No
2 |  |  |  | 0487V126111XC4X33423XXX | 487V#79PG | Standard Plus Automatic Voltage Control and VSSI Reporting | Conformal Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | Screw-Terminal Block | 300 V Phase-Neutral Maximum (Wye), 1 A W , 1 A X Current Terminals | 6 AC Voltage, 6 AC Current | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN, and IEC 61850 | Ethernet Card With One 100BASE-FX, One 10/100BASE-T Connector | 110 Vdc Mainboard configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs, and 7 Optoisolated Level-Sensitive Inputs. | Horizontal Panel Mount | 4U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | No
3 |  |  |  | 0487V126111XC4X3V423XXX | 487V#443C | Standard Plus Automatic Voltage Control and VSSI Reporting | Conformal Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | Screw-Terminal Block | 300 V Phase-Neutral Maximum (Wye), 1 A W , 1 A X Current Terminals | 6 AC Voltage, 6 AC Current | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN, and IEC 61850 | Ethernet Card With One 100BASE-FX, One 10/100BASE-T Connector | 110 Vdc Mainboard configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs, and 7 Optoisolated Level-Sensitive Inputs. | Vertical Rack Mount | 4U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | No
4 |  |  |  | 0487V126111XC4X34423XXX | 487V#6R13 | Standard Plus Automatic Voltage Control and VSSI Reporting | Conformal Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | Screw-Terminal Block | 300 V Phase-Neutral Maximum (Wye), 1 A W , 1 A X Current Terminals | 6 AC Voltage, 6 AC Current | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN, and IEC 61850 | Ethernet Card With One 100BASE-FX, One 10/100BASE-T Connector | 110 Vdc Mainboard configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs, and 7 Optoisolated Level-Sensitive Inputs. | Vertical Panel Mount | 4U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | No
5 |  |  |  | 0487V126111XC2X3H423XXX | 487V#DY09 | Standard Plus Automatic Voltage Control and VSSI Reporting | Conformal Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | Screw-Terminal Block | 300 V Phase-Neutral Maximum (Wye), 1 A W , 1 A X Current Terminals | 6 AC Voltage, 6 AC Current | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN, and IEC 61850 | Ethernet Card With Two 100BASE-FX Connectors | 110 Vdc Mainboard configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs, and 7 Optoisolated Level-Sensitive Inputs. | Horizontal Rack Mount | 4U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | No
6 |  |  |  | 0487V126111XC2X33423XXX | 487V#0LLP | Standard Plus Automatic Voltage Control and VSSI Reporting | Conformal Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | Screw-Terminal Block | 300 V Phase-Neutral Maximum (Wye), 1 A W , 1 A X Current Terminals | 6 AC Voltage, 6 AC Current | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN, and IEC 61850 | Ethernet Card With Two 100BASE-FX Connectors | 110 Vdc Mainboard configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs, and 7 Optoisolated Level-Sensitive Inputs. | Horizontal Panel Mount | 4U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | No
7 |  |  |  | 0487V126111XC2X3V423XXX | 487V#Q95X | Standard Plus Automatic Voltage Control and VSSI Reporting | Conformal Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | Screw-Terminal Block | 300 V Phase-Neutral Maximum (Wye), 1 A W , 1 A X Current Terminals | 6 AC Voltage, 6 AC Current | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN, and IEC 61850 | Ethernet Card With Two 100BASE-FX Connectors | 110 Vdc Mainboard configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs, and 7 Optoisolated Level-Sensitive Inputs. | Vertical Rack Mount | 4U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | No
8 |  |  |  | 0487V126111XC2X34423XXX | 487V#L69G | Standard Plus Automatic Voltage Control and VSSI Reporting | Conformal Coated Circuit Boards | 125-250 Vdc or 110-240 Vac | Screw-Terminal Block | 300 V Phase-Neutral Maximum (Wye), 1 A W , 1 A X Current Terminals | 6 AC Voltage, 6 AC Current | FTP, Telnet, Synchrophasors, DNP3 LAN/WAN, and IEC 61850 | Ethernet Card With Two 100BASE-FX Connectors | 110 Vdc Mainboard configuration has 3 High-Current Interrupting Outputs, 2 Standard Form A Outputs, 3 Standard Form C Outputs, and 7 Optoisolated Level-Sensitive Inputs. | Vertical Panel Mount | 4U, Up to One Additional I/O Board | 8 Optoisolated Independent Level-Sensitive Inputs, 13 Standard Form A, 2 Standard Form C Outputs | 110 Vdc | NA | NA | No

## SEL-751
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Advanced Features | User Interface | Front Panel | Slot A Power Supply Voltage | Slot A Digital Input Voltage | Slot B Ethernet (Port 1) | Slot B Multimode Fiber ST (Port 2) | Slot B Rear Serial Port (Port 3) | IEC 61850 Protocol | DNP3 Protocol | IEC 60870-5-103 Protocol | EtherNet/IP Protocol | Extended IO (Slots 1, 2, 3, 4) | Slot C | Slot C Digital Input Voltage | Slot D | Slot D Digital Input Voltage | Slot E | Slot E Digital Input Voltage | Slot Z Voltage Inputs | Slot Z Current Inputs | Conformal Coat | DMA Bundle
1 | Indoor Switchgear (11kV or 33kV) ARC Flash Protection Device | SEL-751 | 751001DCD0X77831431 | 751001DCD0X77831431 | 751#8GCB | None | English | 2x16 LCD With 4 Pushbuttons | 110-250 Vdc (110-240 Vac); 50/60 Hz | 110 Vdc/Vac | Single 100BASE-FX MM LC Ethernet The protocols SNTP, IEEE 1588-2008 firmware-based PTP and Modbus TCP are included. | Yes | EIA-232 | Yes | Yes | No | No | None | 4 DI / 4 DO Fast High Current Hybrid (Form A) | 110 Vdc/Vac | Empty | NA | 8 Arc-Flash Detection Inputs For Arc-Flash Detection Point Sensors, Bare-Fiber Sensors, or Cable Accessories, see SEL-C804 Multimode Fiber-Optic Arc-Flash Detection (AFD) Sensors and C814 Arc-Flash Detection (AFD) Fiber Cables and Accessories. In order to achieve the 2-5 ms operate times for Arc-Flash Protection a 4 DI/4 DO Fast High Current Hybrid Card is required. | NA | 3-Phase AC Voltage (300 Vac) | 1 Amp Phase, 200 mA Neutral Non-directional relays can order this CT for SEF protection. | Yes | No
2 |  |  |  | 751001DCD0X77831831 | 751#0LP1 | None | English | 2x16 LCD With 4 Pushbuttons | 110-250 Vdc (110-240 Vac); 50/60 Hz | 110 Vdc/Vac | Dual 100BASE-FX MM LC Ethernet The protocols SNTP, IEEE 1588-2008 firmware-based PTP, PRP, and Modbus TCP are included. | Yes | EIA-232 | Yes | Yes | No | No | None | 4 DI / 4 DO Fast High Current Hybrid (Form A) | 110 Vdc/Vac | Empty | NA | 8 Arc-Flash Detection Inputs For Arc-Flash Detection Point Sensors, Bare-Fiber Sensors, or Cable Accessories, see SEL-C804 Multimode Fiber-Optic Arc-Flash Detection (AFD) Sensors and C814 Arc-Flash Detection (AFD) Fiber Cables and Accessories. In order to achieve the 2-5 ms operate times for Arc-Flash Protection a 4 DI/4 DO Fast High Current Hybrid Card is required. | NA | 3-Phase AC Voltage (300 Vac) | 1 Amp Phase, 200 mA Neutral Non-directional relays can order this CT for SEF protection. | Yes | No

## SEL2488
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Time Distribution Protocols | Mounting | Power Supply A | Power Supply B | Ethernet Port (ETH 1, ETH 2) | Ethernet Port (ETH 3, ETH 4) | Holdover | Frequency Outputs | Antenna | Conformal Coat
1 | Satellite-Synchronized Network Clock | SEL-2488 | 24880RAA1181AX23X | 24880RAA1181AX23X | 2488#W1Y2 | IRIG-B, NTP | Horizontal Rack Mount | 125/250 Vdc or Vac | 125/250 Vdc or Vac | 2 10/100BASE-T | 2 10/100BASE-T | TCXO | None | Complete 75ft LMR-400 GPS/GLONASS Installation Kit Includes: (1) GPS/GLONASS Antenna (9524B) (1) 50' Low-Loss LMR-400-FR Cable (C961C-050) (1) 25' Low-Loss LMR-400-FR Cable (C961C-025) (1) Gas Tube Coax Surge Protector and Mounting Kit (915900139) (1) Antenna Pipe-Mounting Kit (915900043) | No
2 |  |  |  | 24880PAA1181AX23X | 2488#W7LV | IRIG-B, NTP | Horizontal Panel Mount | 125/250 Vdc or Vac | 125/250 Vdc or Vac | 2 10/100BASE-T | 2 10/100BASE-T | TCXO | None | Complete 75ft LMR-400 GPS/GLONASS Installation Kit Includes: (1) GPS/GLONASS Antenna (9524B) (1) 50' Low-Loss LMR-400-FR Cable (C961C-050) (1) 25' Low-Loss LMR-400-FR Cable (C961C-025) (1) Gas Tube Coax Surge Protector and Mounting Kit (915900139) (1) Antenna Pipe-Mounting Kit (915900043) | No

## SEL-2414
MR93/2026
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Load Tap Changer Control | Chasis | Front Panel | Slot A Power Supply Voltage | Slot A Digital Input Voltage | Slot B Ethernet | Slot B Fiber-Optic Serial | Slot B IRIG Connector | IEC 61850 Protocol | DNP3 Protocol | Slot C | Slot C Digital Input Voltage | Slot D | Slot D Digital Input Voltage | Slot E | Slot E Digital Input Voltage | Slot Z | Slot Z Digital Input Voltage | Conformal Coat
1 | Transformer Automation Controller (TAC) | SEL-2414 | 241421D6X9X2XE11641 | 241421D6X9X2XE11641 | 2414#55C4 | No | Vertical Panel Mount | Large LCD With 4 Pushbuttons (7 Programmable LEDs) | 125-250 Vdc (120 - 240 Vac) | 110 Vdc/Vac | Dual 10/100 Base -T | Yes | No | Yes | Yes | 4 AI / 4 AO (±20 mA or ±10 V Selectable) | NA | 10 RTD | NA | 8 DO (Standard Form A) | NA | 4ACI/3AVI (1 A Phase, 1 A Neutral, 3-Phase 300 Vac Voltage Input) | NA | Yes

## SEL-3350
SEL RELAY TENDER
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Processor | RAM | Operating System | Client Access Licensee | Conformal Coat | Chasis and Mounting | Power Supply A | Power Supply B | SSD Slot 1 | SSD Slot 2 | Expansion Slot 1 | Expansion Slot 2 | Rear Ethernet Port Configuration | Rear Ethernet Port 1 | Rear Ethernet Port 2 | Rear Ethernet Port 3 | Rear Ethernet Port 4 | Web Human Machine Interface (HMI) | Audit Utilities | IEC 61850 MMS Client and File Services | IEC 61850 MMS Server and File Services | IEC 61850 Goose | EtherNet/IP | Grid Connect Unlimited | Grid Connect Standard | Horizon SVPplus | Horizon Power System Model | Dynamic Disturbance Recorder | Meter Report Trend Recorder | Report Generator/Email Plus | FTP Sync | FileIO | Continuous Recording | Condition Monitoring | OPC UA Server | OPC UA Client | Continuous Waveform Streaming | DER Gateway | OT SDN Flow Controlle | DMA Bundle | DMA Disturbance Monitoring | DMA Configuration Monitoring | DMA Credential Management | DMA Custom Monitoring | DMA Meter Monitoring | DMA Number of Resources (Bundles of 10) | DMS FLISR | FLISR Feeder Quantity | Protocol Services | Protocol Service Data Point Level | SEL Compass | SEL-5030 acSELerator QuickSet | SEL-5033 acSELerator RTAC | SEL-5601-2 Synchrowave Event | SEL-5073 synchroWAVe Phasor Data Concentrator | SEL-5815 PRP Driver for Windows | McAfee - Embedded Control
[6 empty] | Platform | [9 empty] | I/O | [6 empty] | RTAC Software | [20 empty] | Blueframe Applications | [11 empty] | Windows Software
1 | SEL-3350 Automation Controller | SEL-3350 | 3350#83LE |  | 3350#83LE | Intel Atom x5-E3940 Quad Core, 1.6 GHz , -40°C to +85°C | 8 GB ECC RAM | SEL Real-Time Automation Controller (RTAC) The SEL-RTAC product family provides complete and flexible system control with integrated security, seamless configuration, unified logic, and reliability. | None | Conformal Coated Circuit Boards Conformal coating provides protection of electronic circuitry from moisture, fungus, dust and corrosion caused by extreme environments. Solid State Drives and system memory always come conformally coated. | Horizontal 3U Rack Mount | 125-250 Vdc or 110-240 Vac | 125-250 Vdc or 110-240 Vac | SLC 256 GB Industrial Grade SSD SLC SSDs have a 10 year warranty | None For help selecting the best SSD options, refer to Application note AN2016-03. | Serial Expansion Board: 32 RJ45 Ports | Digital IO Expansion Board: 8 Outputs, 24 Inputs | 2 RJ-45 10/100/1000 Mbps, 2 SFP Fiber | RJ45 | RJ45 | SFP 100BASE-FX (1310 nm, Multimode, 2 km) | SFP 1000BASE-ZX (1550 nm, Single-Mode, 80 km) | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes | No | No | No | No | Yes | No | No | No | No | No | No | No | No | None | No | N/A (0) | No | Level 0 | No | No | No | No | No | No | No
2 | [5 empty] | Intel Atom x5-E3940 Quad Core, 1.6 GHz , -40°C to +85°C | 8 GB ECC RAM | SEL Real-Time Automation Controller (RTAC) The SEL-RTAC product family provides complete and flexible system control with integrated security, seamless configuration, unified logic, and reliability. | None | Conformal Coated Circuit Boards Conformal coating provides protection of electronic circuitry from moisture, fungus, dust and corrosion caused by extreme environments. Solid State Drives and system memory always come conformally coated. | Horizontal 3U Panel Mount | 125-250 Vdc or 110-240 Vac | 125-250 Vdc or 110-240 Vac | SLC 256 GB Industrial Grade SSD SLC SSDs have a 10 year warranty | None For help selecting the best SSD options, refer to Application note AN2016-03. | Serial Expansion Board: 32 RJ45 Ports | Digital IO Expansion Board: 8 Outputs, 24 Inputs | 2 RJ-45 10/100/1000 Mbps, 2 SFP Fiber | RJ45 | RJ45 | SFP 100BASE-FX (1310 nm, Multimode, 2 km) | SFP 1000BASE-ZX (1550 nm, Single-Mode, 80 km) | Yes | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes | No | No | No | No | Yes | No | No | No | No | No | No | No | No | None | No | N/A (0) | No | Level 0 | No | No | No | No | No | No | No

## SEL-2902_RJ45 TO DB-9 ADAPTER P
SEL RELAY TENDER
No. | Item Description | Model of IED | Existing Part Number | New Part Number | New Sales Item Number | Mounting | Accessories
1 | SEL-2902 RJ45 to DB-9 Adapter Panel | SEL-2902 | 2902#080B |  | 2902#080B | Adjustable Rack Mount | 2 Foot Ethernet Cable Kit, Qty 16
2 |  |  |  |  | 2902#A22D | Surface Mount | 2 Foot Ethernet Cable Kit, Qty 16